## Radial
| Information |  |  |  | Australia | Bangladesh | Belgium | Brazil | Chile | China | Colombia | Costa Rica | Egypt | Finland | Germany | Great Britain | Honduras | India | Indonesia | Ireland | Italy | Japan | Lebanon | Nepal | North America | Mauritius | Pakistan | Portugal | Puerto Rico | Saudi Arabia | Singapore | Slovenia | South Korea | Sudan | Turkey
| System Section | Characteristic | Sub-category (if applicable) |  | Typical Values |  | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values |  | Typical Values |  | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values |  | Typical Values | Typical Values | Typical Values |  | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values |  | Typical Values
1 | General Characteristics | Frequency |  |  | 50 Hz | 60 Hz | 50 Hz | 60 Hz | 50 Hz | 50 Hz | 60 Hz | 60 Hz | 50 Hz | 50 Hz | 50 Hz | 50 Hz | 60Hz | 50 Hz | 50 Hz | 50 Hz | 50 Hz | 50 Hz(East) and 60 Hz(West) | 50 Hz | 50 Hz | 60 Hz | 50 | 50Hz | 50Hz | 60Hz | 60 Hz | 50 Hz | 50 Hz | 60Hz | 50 Hz | 50 Hz
2 |  | Sources of data |  |  | * Distribution companies reports * AEMC reports * News * Cables manufacturer * Team database | Analysis of publicly available data from 14 utilities and survey conducted for additional information. |  | Analysis of publicly available data from 14 utilities and survey conducted for additional information. | Primary substation data from the independent System Operator (www.coordinador.cl), distribution networks and transformer data from publicly available information from different chilean DNOs (ENEL, CGE, SAESA) | The data come from China's National Energy Administration, local power companies and news reports, e.g., https://www.cec.org.cn/detail/index.html?3-334324 |  | Distribution Network Commission of the College of Electrical, Mechanical, and Industrial Engineers of Costa Rica. Employees of the distribution companies (CNFL, ICE, ESPH, and JASEC) participate in this commission. |  |  |  | Utility open source reports and websites, and GOV.uk online portal | Honduras: https://www.cree.gob.hn/leyes-reglamentos-y-normas-tecnicas/ *https://www.irena.org/Publications/2023/Nov/Renewables-Readiness-Assessment-Honduras Central America: https://crie.org.gt *RMER takes priority over local regulations. | * Distribuiton company database and reports * CEA reports * Discussion with distribution engineers * Government database | PLN (Perusahaan Listrik Indonesia or national electiricy company) standard, national grid code, distribution code, PLN contruction standard, and internal information. | ESB Networks | Terna's Grid Code (TSO) e-Distribuzione (DSO) | TEPCO Assets Planing Rules https://www.tepco.co.jp/pg/consignment/rule-tr-dis/pdf/ryuutu-j.pdf JETEC HP https://www.jectec.or.jp/densen_kiso/denryoku/haiden.html | Électricité du Liban (EDL), www.edl.gov.lb | Electricity Regulation 2050 (Nepal) Grid Code 2080 Utility Reports |  | https:/ceb.mu | By interviewing Transmission and distribution companies employees (LESCO, MEPCO, FESCO , KESCO) |  | Open source and technical papers |  | Open source and technical papers. |  | https://online.kepco.co.kr/TEM001D00
| System Section | Characteristic | Sub-category (if applicable) |  | Typical Values |  | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values |  | Tpical Valuea |  | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values |  | Typical Values | Typical Values | Typical Values |  | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Examples Values |  | Typical Values
3 | Substation | Voltages (line-to-line) | High side |  | 33, 66 kV | 69, 138, 230 kV | 36, 70 kV | 69, 138, 230 kV | 44, 66, 110, 154 kV | 35, 66, 110 kV | 57.5, 66, 110, 115, 230, 500 kV | 138, 230 kV | 33, 66, 132, 220, 500 kV | 110 kV | 10, 20, 100, 220, 380 kV | 132 kV | 69,138,230 kV | 33, 66 kV | 66, 150 kV | 38, 110 kV | 36, 60, 132, 150, 220, 380 kV | 22, 33, 77, 154 kV | 66 kV (some areas up to 150 or 220 kV) | 33, 66, 132 kV | 69, 115, 230, 345, 500, 765 kV | 66 kV | 220, 500 kV | 60 kV | 38, 115, 230 kV | 69, 115, 230, 380 kV | 66 kV | 69, 115, 230, 380 kV | 154, 345, 765 kV | 66, 110, 220, 550 kV | 154, 380 kV
|  |  | Low Side |  | 6.6, 11, 22, 33 kV For SWER: 12.7, 19 kV | 11.9, 13.8, 23.1, 34.5 kV | 10, 11, 12, 15, 26, 29.9 kV | 11.9, 13.8, 23.1, 34.5 kV | 12, 13.2, 13.8, 15, 23 kV | 10 kV | 11.4, 13.2, 13.8, 34.5, 44.0 kV | 13.2, 13.8, 24.0, 34.5 , 69 kV | 11, 22 kV | 10, 20 kV | 0.4, 10, 20, 110, 220 kV | 6.6, 11, 33 kV | 13.8 , 34.5 kV | 2.2, 3.3, 6.6, 11, 22, 33 kV 11 kV is the most common | 20 kV | 10.7, 21.5 kV | 10, 11, 15, 20, 22 kV | 6.6, 33, 66 kV | 15 kV typical, 11 kV and 20 kV in some areas | 11 kV | 4.2, 6.6, 11.0, 12.47, 13.2, 13.8, 23.0, 33.0, 34.5kV | 6.6, 22 kV | 11, 66, 132 kV | 10, 15, 30 kV | 4.16, 4.8, 7.2, 8.32 13.2kV | Standard: 12.47, 13.8, 33 kV, 34.5kV, 11 kV Existing but not standard 11, 34.5 kV | 22 kV | 10.0, 20.0 kV | 22.9 kV | 11, 33 kV | 15.8, 34.5 kV
4 |  | Operational Topology |  |  | Single Bus | Single Bus Double Bus | Single Bus Ring Bus Breaker and a half Bus Hybrid | Single Bus Double Bus | Single Bus Sectionalized Bus Main and transfer Bus | Single Bus | Single Bus Double Bus (uncommon) | Single Bus Double Bus | Single Bus Double Bus Breaker and a half Bus | Single Bus Double Bus | Data was not readily found. | Ring Bus Split Bus | Single Bus Sectionalized Bus Main and transfer Bus | Single Bus Double Bus Open ring (redundancy) | Single Bus Double Bus | Single Bus Split Bus Double Busbar (Dublin 110 kV Substations) | Single Bus Double Bus | Single Bus | Radial with normally open tie switches for reconfiguration | 33 kV- Single busbar 66 kV- Single busbar in rural; Double busbar in urban 132 kV- Double bus bar | Single Bus Ring Bus Breaker and a half Bus Hybrid | Single Bus Double Bus Ring Bus | Single Bus Double Bus Breaker and a Half Bus | Single Bus | Single Bus (most prevalent) Double Bus (less prevalent) | Single Bus Ring Bus Breaker and a Half Bus Double Bus Single Breaker | Single Bus Double Bus | Single Bus Double Bus Ring Bus | Single Bus Double Bus Ring Bus | Breaker and a half Single Bus Double Bus | Breaker and a half Single Bus Double Bus Ring Bus
5 |  | Typical MVA (total) |  |  | 5-250 MVA | 5-50 MVA | 25-150 MVA | 5-50 MVA | 10-75 MVA | 35 kV: 60 MVA 66, 100 kV: 80MVA | Rural, industrial: 0.5-10 MVA Urban: Up to 90 MVA | 90 MVA | 40, 80, 120, 175, 250, 500, 750, 1000, 1500MVA | 200 MVA-600 MVA | 50-250 MVA | 60-240 MVA | 50-150 MVA | 10-250 MVA | 15-240 MVA | 10-150 MVA | 50-130 MVA | 20-90 MVA | 40-80 MVA | 8, 16, 30, 45, 60 MVA | 5-500 MVA | 45MVA | 20-200 MVA | 20-80 MVA | 5-15MVA, with 7.5MVA the most common. | 15-20 MVA 25-30 MVA | 150 MVA | Data not available | 12-8000 MVA | 5, 15, 20, 60, 80, 100, 150, 300 MVA | 25, 50, 100, 250, 300, 500 MVA
6 |  | Transformer Connections |  |  | Delta-Delta Delta-Wye Wye-Delta Wye-Wye | Delta-Delta Delta-Wye (mostly) Wye-Delta Wye-Wye | Wye-Wye | Delta-Delta Delta-Wye (mostly) Wye-Delta Wye-Wye | Delta-Wye (grounded) | Wye-Delta | Delta-Wye | Wye-Delta Wye-Wye | Delta-Wye (grounded) Delta-Delta | Wye-Wye | Delta-Wye | Delta-Wye Delta-Delta | Delta-Wye (mostly) Wye-Delta Wye-Wye | Delta-Delta (most common) Wye-Delta | Wye-Delta | Delta-Delta Wye-Delta | Wye-Delta Wye-Wye | Wye-Delta | Wye-Delta Wye-Wye (grounded) | 132/11 kV- Wye-Wye 66/11 kV- Wye-Wye 33/11 kV- Delta-Wye 11/0.4 kV- Delta-Wye | Delta-Delta Delta-Wye Wye-Delta Wye-Wye | Delta-Delta | Delta-Delta Delta-Wye Wye-Delta Auto Transformers | Wye-Delta Wye-Wye | Dela-Wye (grounded) most common Wye-Wye (grounded) less common | Delta-Wye Wye-Wye | Wye-Delta | Delta-Delta or Delta-Wye or Wye-Delta or Wye-Wye | Wye-Delta Delta-Delta | 33/11 kV: Delta-Wye 66/11 kV: Delta-Wye 220/110 kV or 500/220 kV: Wye-Delta | 66/11 kV or 66/22 kV: Delta-Wye 154/11 kV or 154/15.8 kV: Wye-Delta 154/33 kV: Wye-Delta 220/66 kV: Wyw-Wye 380/154 kV: Wye-Wye or Wye-Delta
7 |  | Typical Transformer MVA (individual) |  |  | 10, 13, 15, 20, 25, 33, 40, 45, 57, 90, 100 MVA | 10, 15, 20, 25, 30, 50, 74 MVA | 25-50 MVA | 10, 15, 20, 25, 30, 50, 74 MVA | 10, 12.5, 15, 20, 22.4, 25, 30 MVA | 35 kV: 10, 20, 31.5 MVA 66 kV: 31.5, 40, 50 MVA 110 kV: 40, 50 63 MVA | 0.25, 0.8, 1, 2, 2.5, 5, 10, 12.5, 15, 20, 22.4, 25, 30 MVA | 30, 45 MVA | 2.5, 5, 10, 15, 20, 25, 30, 40 50, 60, 75, 100 MVA | 31.5, 40 MVA | 10, 20, 31.5 MVA | 15, 21 MVA | 15, 20, 25, 30, 50, 75 MVA | 3.5, 5, 10, 16, 20, 25, 31.5, 40 MVA | 15, 30, 60 MVA | 10 MVA | 25, 40, 63 MVA | 10, 20, 30 MVA | 10-40 MVA | 33/11 kV-3, 8 MVA 66/11 kV- 15 MVA, 30 MVA 132/11 kV- 22.5, 45 MVA | 5, 10, 25, 50 100 MVA | 45MVA | 10, 13, 20, 26, 31, 40, 150, 200 MVA | 20.0, 31.5, 40.0 MVA | 7.5 and 11.3 MVA | 15, 20, 25, 30 MVA | 150 MVA | 5, 10, 15, 25, 35, 50, 60, 75, 100 MVA | 154 kV: 60 MVA 345 kV: 500 MVA 765 kV: 2000 MVA | 2.5, 5, 10, , 20, 25, 35, 40 .50, 60, 80, 100, 150, 300 MVA | 33/0.4 kV: 0.4–2.5 MVA 154/11 kV and 154/15.8 kV: 25–63 MVA 154/33 kV: 25–100 MVA 380/154 kV: 250–500 MVA
8 |  | Range of Short-circuit level |  |  | 1 kV: <50 kA 6.6 kV: <21.9 kA 11 kV: <18.4 kA 22 kV: <13.1 kA 33 kV: <25 kA 66 kV: < 25 kA 132 kV: < 40 kA | 5-20 kA | 5-15 kA | 5-20 kA | 6-15 kA | 220kV：40-50kA 110kV: 31.5-40kA | 10-40kA | 13.2 kV - 10 kA 13.8 kV - 10 kA 24.9 kV - 8 kA 34.5 kV - 8 kA 69 kV - 5 kA | 11 kV: 26.24 kA 22 kV: 19.68 kA 66 kV: 13.12 kA 66 kV: 21.87 kA | 40 kA 110 kV, 25/20 kA 10/20 kV level | Data was not readily found. | 5-27 kA | 5-27 kA | 11 kV: ~15 kA 33 kV: ~ 20 kA | 66 kV: 25 kA 150 kV: 31.5 kA, 40 kA | 4.5-11 kA | 380 kV: ~10-45 kA 220 kV: ~4-34 kA 150 kV: ~4-17 kA 132 kV: ~3-25 kA | 6.6 kV: 12.5 kA 22 kV: 25kA 33, 66, 77 kV: 31.5kA | 15 kV: 10-15 kVA 66 kV: 7-8 kA | 132 kV- 40 kA 66 kV- 40 kA 33 kV- 31.5 kA 11 kV- 25 kA | 10-100 kVA | 25kA (22kV S/s) | 500 kV: ~40-63 kA 220 kV: ~31.5-50 kA 132 kV: ~20-31.5 kA 66 kV: ~16-25 kA 33 kV: ~13-20 kA 11 kV: ~8-16 kA | 25 kA | 35kA to 7.5kA at 115kV/230kV; median 12kA 19kA to 7.5kA at 38kV; median 11kA | 11, 13.8 k V: 21 kA 33, 34.5 kV: 25 kA | 25 kA | 5-10 kA | 31.5, 40, 50, 63 kA | Data was not readily found. | 0.4 kV: 6–16 kA 11–15.8 kV: 16–25 kA 33 kV: 16–25 kA 154 kV: 25–40 kA
9 |  | Voltage Regulation Devices |  |  | On-load Tap Changers (OLTC) Shunt Capacitors | On-load Tap Changers (OLTC) Shunt Capacitors | On-load Tap Changers (OLTC) | On-load Tap Changers (OLTC) Shunt Capacitors | On-load Tap Changers (OLTC) Shunt Capacitors | On-load Tap Changers (OLTC) Shunt Capacitors Voltage Regulators | On-load Tap Changers (OLTC) Shunt Capacitors Voltage Regulators | On-load tap changer (OLTC) | On-load Tap Changers (OLTC) Voltage Regulators | On-load tap changer (OLTC) | On-load Tap Changers (OLTC) Shunt Capacitors Static var Compensators | On-load Tap changer (OLTC) | On-load Tap Changers (OLTC) Shunt Capacitors | On-load Tap Changers (OLTC) Sunt Capacitors | On-load Tap Changers (OLTC) Shunt Capacitors | On-load Tap Changers (OLTC) | On-load Tap Changers (OLTC) | On-load Tap Changers (OLTC) Shunt Capacitores | On-load Tap Changers (OLTC) Shunt Capacitors | Avanced Power Flow Controllers (APFC) On-load Tap Changers (OLTC) Shunt Capacitors | On-load Tap Changers (OLTC) Shunt Capacitors Voltage Regulators | On-load Tap Changers (OLTC) | On-load Tap Changers (OLTC) Shunt Capacitors Voltage Regulators | On-load Tap Changers (OLTC) Shunt Capacitors | On-load Tap Changers (OLTC) Shunt Capacitors Voltage Regulators | On-load Tap Changers (OLTC) Shunt Caacpitores Shunt Reactors | On-load tap changer (OLTC) | Manual Tap Changers On-load Tap Changers (OLTC) | On-load Tap Changers (OLTC) Shunt Capacitors | On-Load Tap Changer (OLTC) Shunt Reactors Shunt Capacitors Voltage Regulators | On-Load Tap Changer (OLTC) Shunt Reactors Shunt Capacitors Static VAR Compensator (SVC) Voltage Regulator
10 |  | Protection Devices |  |  | Circuit Breakers Switches | Circuit Breakers Fuses Reclosers | Circuit Breaker Fuse Reclosers | Circuit Breakers Fuses Reclosers | Circuit Breakers Reclosers | Circuit Breakers | Circuit Breakers Fuses Reclosers | Circuit Breakers Fuses Lightning Arresters | Circuit Breakers Fuses Lightning Arresters Reclosers | Circuit Breakers | Circuit Breaker Fuses Lightning Arresters | Circuit Breakers | Circuit Breakers Reclosers | Circuit Breakers | Circuit Breakers Fuses Reclosers | Circuit Breakers | Circuit Breakers | Circuit Breakers Lightning Arresters | Circuit Breakers | Circuit Breakers | Circuit Breakers Fuses Lightning Arresters Reclosers | Circuit Breakers Fuses Reclosers | Circuit Breakers Fuses Lightning Arresters Reclosers | Circuit Breakers | Circuit Breakers (less than 1/3 of the substations) Fuses (most of the substations - over 2/3) | Circuit Breakers Reclosers | Circuit Breakers | Circuit Breakers Fuse Reclosers | Circuit Breakers Fuses Reclosers | Circuit Breakers Fuses Reclosers Surge Arresters | Circuit Breakers Fuses Surge Arresters
11 |  | SCADA/ Control | Media |  | Cellular (3G and 4G) Fiber Optic Cable | Cellular (3G and 4G) Fiber Optic Cable | Cellular (4G) Coaxial Fiber Optic Cable | Cellular (3G and 4G) Copper Cable Fiber Optic Cable | Cellualr (3G) Radio (General Packet Radio Service) | Cellular (4G and 5G) Fiber Optic Cable | Cellular (3G and 4G) Fiber Optic Cable | Fiber Optic Cable | Cellular (3G and 4G) Fiber Optic Cable | Fiber Optic Cable | Data was not readily found. | Cellular (3G and 4G) Fiber Optic Cable Microwave | Copper Cable Fiber Optic Cable | Fiber Optic Cable | Cellular (4G) Fiber Optic Cable | Cellular (3G and 4G) Fiber Optic Cable Satellite | Fiber Optic Cable Wireless Power Line Carrier | Cellular (3G and 4G) Copper Cable Fiber Optic Cable | Cellular (4G) Fiber Optic Cable | Fiber Optic Cable | Cellular (4G and 5G) Copper Cable Fiber Optic Cable Microwave Power Lne Carrier (PLC) Satellite Radio Telephone WiMax | Cellular (4G and 5G) Copper Cable Fiber Optic Cable Power Line Capprier (PLC) | Cellular (3G and 4G) Fiber Optic Cable Microwave Power Line Carrier (PLC) Satellite Radio, Ethernet/IP-Based Communication | Cellular (4G and 5G) Fiber Optic Cable (preferred method and the most common) | Cellular (4G and 5G) Copper Cable Fiber Optic Cable Power Line Carrier (PLC) | Copper Cable Fiber Optic Cable | Fibre Optic Cable in 66 kV | Cellular (3G) Fiber Optic Cable | Cellular (4G and 5G) Copper Cable Fiber Optic Cable Power Line Carrier (PLC) | Fiber Optic Cable Power Line Carrier (PLC) | Copper Cable Fiber Optic Cable Microwave
|  |  | Measured Information and Cycle |  | Active Power Current Reactive Power Status (breaker, recloser, switch) Voltage Cycle: Data was not readily found. | Active Power Current Reactive Power Status (breaker, recloser, switch) Voltage Cycle: Data was not readily found. | Active Power Current Reactive Power Voltage Cycle: Differential, when value change. | Active Power Current Reactive Power Status (breaker, recloser, switch) Voltage Cycle: Data was not readily found. | Active Power Current Reactive Power Status (breaker, recloser, switch) Voltage Cycle: Data was not readily found. | Active Power Current Reactive Power Status (breaker, recloser, switch) Voltage Cycle: 5 seconds | Active Power Current Reactive Power Status (breaker, recloser, switch) Voltage Cycle: Data was not readily found. | Active Power Current Reactive Power Status (breaker, recloser, switch, etc.) Voltage Cycle: 5 seconds | Active Power Current Reactive Power Voltage Cycle: 2-300 seconds | Active Power Current Reactive Power Voltage Cycle: Differential, when value change. | Data was not readily found. | Active Power Current Reactive Power Status (breaker, recloser, switch, etc.) Voltage Cycle: Data was not readily found. | Active Power Current Reactive Power Status (breaker, recloser, switch) Voltage Cycle: Data was not readily found. | Active Power Reactive Power Status (breaker) Voltage Voltage and current THD Frequency Cycle: One second. | Active Power Current Reactive Power Status (breaker, recloser, switch) Voltage Cycle: Data was not readily found. | Active Power Current Reactive Power Status (breaker, recloser, switch, etc.) Voltage Cycle: Data was not readily found. | Voltage Current Active and Reactive Power Status (breaker, recloser, switch, OLTC, etc.) Cycle: 1-4 seconds (0.2 seconds for protection tripping and alarms) | Active Power Current Reactive Power Status (breaker, recloser, switch, etc.) Voltage Cycle: 1-60 second (depend on types of measurement) | Current Status (breaker, recloser, switch, etc.) Voltage Cycle: Every few seconds. | Data was not readily found. | Active Power Current Reactive Power Status (breaker, recloser, switch, etc.) Voltage Cycle: 3-5 seconds for SCADA, 30-60 samples/second for PMU. | Active Power Current Reactive Power Voltage Cycle: Data was not readily found. | Active Power Current Reactive Power Status of breaker, recloser, switch Voltage Cycle: by exception, typically 2-300 seconds. | Active Power Current Reactive Power Status (breaker, recloser, switch, etc.) Voltage Cycle: 30 seconds | Active Power Reactive Power Voltage Cycle: 2 seconds | Active Power Current Reactive Power Voltage Cycle: 4 seconds | Data was not readily found. | Active Power Current Reactive Power Voltage Cycle: Differential, when value change. | Voltage Cycle: 30 seconds | Data was not readily found. | Active Power Current Reactive Power Voltage Cycle: 2-10 seconds for SCADA, 30-60 samples/second for PMU.
|  |  | Available Control type |  | Open/close breaker, switch, and/or recloser Raise/lower regulator or OLTC | Capacitor controls Open/close breaker, switch, and/or recloser Raise/lower regulator or OLTC | Data was not readily found. | Capacitor controls Open/close breaker, switch, and/or recloser Raise/lower regulator or OLTC | Capacitor controls Open/close breaker, switch, and/or recloser Raise/lower regulator or OLTC | Capacitor controls Open/close breaker, switch, and/or recloser Raise/lower regulator or OLTC | Capacitor controls Open/close breaker, switch, and/or recloser Raise/lower regulator or OLTC | Open/close breaker, switch, and/or recloser Protection on/off | Open/close breaker, switch, and/or recloser Raise/lower regulator or OLTC | Open/close breaker, switch, and/or recloser | Data was not readily found. | Open/close breake or recloser Protection on/off | Capacitor controls Open/close breaker, switch, and/or recloser Raise/lower regulator or OLTC | Open/close breaker, switch, and/or recloser Raise/lower regulator or OLTC | Capacitor controls Open/close breaker, switch, and/or recloser Raise/lower regulator or OLTC | Open/close breaker, switch, and/or recloser | Open/close breaker, switch, and/or recloser Raise/lower regulator or OLTC | Capacitor controls Open/close breaker, switch, and/or recloser Raise/lower regulator or OLTC | Open/close breaker, switch, and/or recloser Raise/lower regulator or OLTC | Data was not readily found. | Capacitor controls Open/close breaker, switch, and/or recloser Pole smart meter Raise/lower regulator or OLTC | Open/close breaker, switch, and/or recloser | Capacitor controls Open/close breaker, switch, and/or recloser Raise/lower regulator or OLTC | Capacitor controls Open/close breaker, switch, and/or recloser Raise/lower regulator or OLTC | Open/close breaker, switch, and/or recloser Raise/lower regulator or OLTC | Capacitor controls Open/close breaker, switch, and/or recloser Raise/lower regulator or OLTC | Open/close breaker, switch, and/or recloser Raise/lower regulator or OLTC | Open/close breaker, switch, and/or recloser Ping smart meter Raise/lower regulator or OLTC | Open/close breaker, switch, and/or recloser Raise/lower regulator or OLTC | Open/close breaker Raise/lower regulator or OLTC | Capacitor controls Open/close breaker, switch, and/or recloser Raise/lower regulator or OLTC
|  |  | Communication Protocol |  | DNP 3.0 ICCP IEC 61850 | DNP 3.0 IEC 61850 | ICCP IEC 104 MODBUS | DNP 3.0 IEC 61850 | DNP 3.0 IEC 61850 | DNP 3.0 IEC 61850 | DNP3.0 IEC 61850 Modbus | DNP 3 ICCP IEC 61850 IEC 60870-104 Modbus | DNP 3 IEC 60870-104 IEC 61850 IEC 60870-101 Modbus | IEC 60870-104 | Data was not readily found. | DNP3 FTP IEC 61850 MODBUS | DNP 3.0 IEC 61850 | IEC 60870-104 (most common) ModBus TCP/ IP RS485 | DNP 3.0 IEC 60870-101 IEC 60870-104 IEC 61850 | IEC 60870-101 | IEC60870-104 | Custom/Proprietary IEC 61850 | DNP3 IEC 60870-104 IEC 61850 | Data was not readily found. | Custom/Proprietary DNP3 GOOSE ICCP IEC 60870 IEC 61850 IEEE 802.3/802.2 Modbus TCP/IP | IEC 104 | NP 3 IEC 60870 IEC 61850 Modbus, | IEC 104 IEC 61850 | DNP 3 | IEC 61850 | IEC 101 | DNP 3 ICCP IEC 104 Modbus | DNP 3 IEC 61850 | IEC 60870-101 IEC 60870-104 Modbus | DNP 3 IEC 61850 IEC 60870-104 MODBUS OPC / OPC UA
| System Section | Characteristic | Sub-category (if applicable) |  | Typical Values |  | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values |  | Typical Valiues |  | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values |  | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values |  | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Valiues | Typical Values
12 | Primary | Common Voltage Levels (line-to-line) |  |  | 6.6, 11, 22, 33 kV For SWER: 12.7, 19 kV | 11.4, 11.9, 13.8, 23.1, 34.5 kV | 10, 11, 12, 15 kV | 11.4, 11.9, 13.8, 23.1, 34.5 kV | 12, 13.2, 13.8, 15, 23 kV | 10 kV | 4.16, 11.4, 13.2, 13.8, 34.5 kV | 13.2, 13.8, 24.9, 34. 5, 69 kV | 11, 22 kV | 10, 20 kV | 10 kV | 6.6, 11, 33 kV | 13.8, 34.5 kV | 11, 33 kV 11 kV is the most common | 20 kV | 10, 20 kV | 15, 20 kV other values 10, 11, 13, 22 kV | 6.6, 22, 33 kV | 11, 15, 20 kV legacy 5.5 kV | 11 kV, 33 kV | 4.2, 6.6, 11.0, 12.47, 13.2, 13.8, 23.0, 33.0, 34.5kV 12.47 is the most common | 22 kV | 132, 220, 500 kV | 10, 15, 30 kV | 4.16, 4.8, 7.2, 8.32, 13.2 kV | Standard: 12.47, 13.8, 33 kV Existing but not standard 11, 34.5 kV | 6.6, 22 kV | 10, 20 kV | 22.9 kV | 11, 33 kV | 15.8, 33 kV
13 |  | Grounding Method |  |  | Common Multiple Earthed Neutral (CMEN) Low Voltage Multiple Earthed Neutral (MEN) Separately Earthed System | Three wire grounded at SE (unigrounded) and three wire multigrounded | Global earthing | Three wire unigrounded for primary (MV) and four wire with common multiple earthed neutral (multigrounded system) | Three wire ungrounded for primary (MV) and four wire grounded for secondary (LV) | Three wire ungrounded Low resistance grounded Arc suppression coil grounded | Four wire grounded | Four wire grounded | Four wire grounded Three wire ungrounded | Four wire grounded Three wire ungrounded (20 kV Petersen coil) | Data was not readily found. | Four wire grounded | Four wire grounded | Four wire grounded | Solid grounded Neutral Grounding Resistor Multi grounded common netral | Four wire grounded Three wire ungrounded | Petersen coil | 22, 33 kV: Four wire grounded 6.6 kV: Three wire ungrounded | Four wire grounded, with grounding resistor | Three wire ungrounded | Four wire grounded Three wire ungrounded (legacy) | Three wire ungrounded | Mesh earthing system Neutral grounding Four wire neutral grounding | Four wire grounded (Low Impedance) | Four wire grounded | Four wire grounded | 6.6 kV: Four wire grounded (Low Impedance) 22 kV: Four wire grounded (solid) | Four wire grounded | Four wire grounded Three wire ungrounded | <400 V: Four wire grounded 11, 33 kV: Three wire ungraounded | Four wire grounded Three wire ungrounded
14 |  | Operational Topology |  |  | Radial | Radial | Radial (Open-Loop) | Radial | Radial Radial (Open-Loop) | Radial Weakly meshed | Radial Radial (Open-Loop) | Open ring Radial | Rural: Radial Urban: Radial (Open-Loop) | Radial (Open-Loop) | Radial Meshed | Radial | Radial (rural) Open-Loop (urban) | Radial | Ovehead: Radial and Radial (Open-Loop) Underground: Weakly meshed | Radial | Radial | Radial | Radial (Open-Loop) | Radial | Radial Radial (Open-Loop) | Meshed Radial | Radial Radial (Open-Loop) | Radial | Radial | Radial | 6.6 kV: Open loop 22 kV: Closed loop | Open ring Radial | Meshed Networked Radial | Radial | Radial Radial (Open-Loop)
15 |  | Level of Unbalance |  |  | <2-3% | <2% | 4% | <2% | High density: <=2% Other: <=3% | 2-4% | Residential: < 15% (current) | <3% | <1% | < 1 % (voltage) | Data was not readily found. | <2% | < 15% | <3% (at DT level) | <2% | Based on NMS data: Typically 0-10% 75% of feeders 0-15% 80-85% of feeders 0-20% | No data | <3% | 2-3% allowed; can exceed 3% in practice | Data was not readily found. | 0-10%, typically <3%. | <6% | Urban Areas: 2-5% Rural Areas : 5-10% | <3% | >40% (current) | <1% | <3% | 3-5% | <10% | <5% | ≤ 1%
16 |  | Reliability Index (SAIDI) |  |  | Rural: <140 Urban: <200 Urban Networked: <4 | 300-600 >2000 in some regions | 20 | 300-600 >2000 in some regions | 400-500 | 2023 data: Rural: 544 Urban: 128 | 2021 data: 2.5-107.6, Average of 28.84 | 2023: 502 | <12 | 3-4 | Data was not readily found. | <60 | 2023 data: 32.5 | 2021: 168 2022: 107 2023: 116 2024: ~100 2025: ~ 80 (govt target) 2026: ~60 (govt target) | Cluster 1: <150 Cluster 2: 150-250 Cluster 3: 250-350 | 2021 and 2022 Data: 2021: 95.99 2022: 103.34 | 40 (average) | 2021 and 2022 data: 2021: 10 2022: 25 | >8000 | Not calculated; ERC is yet to mandate the utility to calculate and report these parameters | ~300 w major events; ~120 w/o major events | Data was not readily found. | SAIDI (Minutes/Year) LESCO (Lahore): 700–1,200 IESCO (Islamabad): 500–1,000 FESCO (Faisalabad): 800–1,500 MEPCO (Multan): 1,200–2,000 HESCO (Hyderabad) : 2,000–2,500 K-Electric (Karachi) : 900–1,500 | 61 | > 1,000 | 2023 and 2024 data: 2023: 82.16 2024: 33.46 | 2021 data: 2021: 0.13 | 60 | 2024 data: 2024: 18.6 | Data was not readily found. | Rural: ~150–600 Urban: ~50–150
17 |  | Typical Feeder length |  |  | Non-rural: MV feeders: average is 72 km Rural: (usually supplied by SWER lines): average 156 km MV feeders (rural + non-rural): average 110 km | 2-100 km | 500-7000 m | 2-100 km | 10-100 km | 10-15 km | 15-25 km | Rural: 30 km Urban: 5 km | 60-100 km | 2.5 km | 0.5-160 km | Rural: 10-30 km Urban: 2-5 km | Rural: 50-70 km Urban: 10-25 km | Rural: <= 20 km Urban: <=4 km | Overhead: <150 km Underground: Typically <8 km in Urban | 16.34 km at the Mullingar/Tullamore MV area | 13-15 km | Rural: 2-5 km Urban: <60 km | Rural: <20 km Urban: 2-5 km | Rural:15 to 100+ km Urban: 5 to 15 km | Rural: 1-75 km Urban: 1-15 km | Data was not readily found. | Rural: 50-60 km Urban: 10-15 km | 15 kV: 30 km 30 kV: 60 km | 15 km average, but can exceed 150 km | 30 km | 6.6 kV: <15 km 22 kV: <30 km | 200-500 m | Data was not readily found. | Data was not readily found. | Rural: 20–50 km Suburban: 10–20 km Urban: 2–10 km
18 |  | Typical Types of Conductors |  |  | Overhead: bare wire Steel, 3/2.75 ACSR, 3/4/2.5, 6/1/2.5, 6/1/3.0, 6/1/3.75, 6/4.75/, 7/1.60 AAC, 7/2.5, 7/3.0, 19/3.25, 19/3.75, 37/3.75, 7/4.75, 19/4.75 Underground: XLPE Al: 35, 185, 249, 300 mm2 | Data was not readily found. | Data was not readily found. | Aluminium; 1/0 AWG; 4/0 AWG; 336,4 MCM; 477 MCM; spacer cable: 35 mm2; 50 mm2; 70 mm2; 150 mm2; 185 mm2; multiplex: 3x240 + 1x120 mm2 | Most common: Al: 185, 300 mm2 Cu: 6 AWG | Most common: Overhead: 220kV:JL/LB1A-630/45 JNRLH60/LB14-630/45 JL/LBIA-400+LGJ-400 110kV:LGJ-300-110kV 35kV:LGJ-300-35kV LGJ-150-35kV LGJ-95-35kV LGJ-70-35kV 10kV:JKLGYJ-10-240/30 Underground: YJV、YJV22、YJV32、YJV42 | Data was not readily found. | Overhead: AAAC 123.3 kcmil ~ 559.5 kcmil AAC 3/0 AWG ~ 477 kcmil Underground: EPR 1/0 AWG ~ 500 kcmil | AAC: 405 ACSR: 25/150, 40/240, 50/380 | Data was not readily found. | Data was not readily found. | Overhead: ACSR (95 mm2 to 300 mm2), AAAC (100 mm2 to 300 mm2) Underground: Aluminuim XLPE insulated cables (95 mm2 to 400 mm2), Copper XLPE insulated cables (95 mm2 to 300 mm2) | Overhead: ACSR 4/0 AWG ~ 477 kcmil AAC 6 AWG ~ 556 kcmil Underground: XLPE 1/0 AWG ~ 1000 kcmil EPR 1/0 AWG ~ 1000 kcmil | Overhead: ACSR: Racoon, Dog, Rabbit common Underground: XLPE Al: 150, 240, 300, 400 mm2 | Overhead: AAAC-S 150 mm2 and 70 mm2 Underground: XLPE Al: 150, 240 and 300 mm2 | Overhead: Steel core aluminium (SCR) 50 and 92 Underground: XLPE 185 and 400 | Overhead: Al - bare: 35, 70, 150 mmq Cu - bare: 16, 25, 35, 70 mmq Al - XLPE: 25, 50, 95, 150 mmq Underground: Al - XLPE/PVC 95, 150, 185, 240 mmq Cu - XLPE/PVC 50, 95, 150 mmq | Overhead: ACSR 120 or 32 mm2 | Overhead: AAC: 122-475 kcmil ACSR: 122-475 kcmil Underground XLPE, ABC at LV: 122-475 kcmil | Overhead: ACSR DOG (100 sq. mm) RABBIT (50 sq. mm) Underground: XLPE (95 sq.mm, 120 sq.mm) | Overhead: Bare conductor AAC: Up to 1000 kcmil ACSR: Up to 1000 kcmil Cu: Up to 1 kcmil Underground: XLPE Cu: Up to 1000 kcmil | AAAC 22 kV: 336 kcmil 66 kV: 150 kcmil | Overhead Conductors, AAC:250-1000kcmil ACSR : Up to 1000 kcmil (Dog : 266.8 kcmil, Wolf: 477 kcmil, Panther: 795 kcmil – 1000 kcmil), AAAC, Underground Cables: XLPE: Copper and Aluminium Core (Cu) : 250-1000 kcmil | Overhead: ACSR: 70 to 160 mm2 Underground; CU: 240mm2 | Overhead: Bare conductor AAC: Up to 1000 kcmil ACSR: Up to 1000 kcmil Cu: Up to 1000 kcmil Underground: XLPE Cu: Up to 1000 kcmil | Data was not readily found. | Overhead: Most common types are 300 mm2 Cu, 300 mm2 Al and 185 mm2 Al Underground: XLPE/SWA/PVC | Data was not readily found. | Overhead: ACSR 4/0 AWG ~ 954 kcmil AAC 6 AWG ~ 795 kcmil Underground: XLPE 1/0 AWG ~ 2500 kcmil PVC 2 AWG ~ 1000 kcmil EPR 1/0 AWG ~ 2500 kcmil | Data was not readily found. | Data was not readily found.
19 |  | Voltage Regulation Devices |  |  | On-load Tap Changers (OLTC) Shunt Capacitors Voltage Regulators | Shunt Capacitors Voltage Regulators | Usually none | Shunt Capacitors Voltage Regulators | Shunt Capacitors Voltage Regulators | Shunt Capacitors Voltage Regulators | Shunt Capacitors Voltage Regulators | Voltage Regulators | On-load Tap Changers (OLTC) Voltage Regulators | On-load Tap Changers (OLTC) (100%) | On-load Tap Changers (OLTC) Voltage Regulators | On-load Tap Changers (OLTC) Voltage Regulators | On-load Tap Changers (OLTC) Shunt Capacitors | Shunt Capcitors Voltage Regulators | Shunt Capacitors | Voltage Regulators | Off-load Tap Changer (MV side) | Voltage Regulators | Shunt Capacitors | Shunt Capacitors | Shunt Capacitors Voltage Regulators | Shunt Capacitors Voltage Regulators | On-load Tap Changers (OLTC) Shunt Capacitors | On-load Tap Changers (OLTC) at the primary susbtation Changeable tap at the secondary substation (no OLTC, manual operation) | Shunt Capacitors Voltage Regulators | On-load Tap Changers (OLTC) Shunt Capacitors | 66/22 kV station: On-load Tap Changers (OLTC) | On-load Tap Changers (OLTC) | Shunt Capacitors Voltage Regulators | On-Load Tap Changer (OLTC) Shunt Reactor Shunt Capacitor Bank Voltage Regulator | On-Load Tap Changer (OLTC) Shunt Reactor Shunt Capacitor Bank Static VAR Compensator (SVC) Voltage Regulator
20 |  | Protection Devices |  |  | Circuit Breakers Switches Reclosers | Fuses Reclosers Sectionalizers | Fuses Relay | Fuses Reclosers Sectionalizers | Fuses Reclosers | Reclosers | Fuses Reclosers Sectionalizers | Fuses Reclosers | Circuit Breakers Fuses Lightning Arrester Reclosers | Fuse towards distribution transformer | Circuit Breaker Fuses Lightning Arresters | Circuit Breakers Reclosers | Circuit Breakers | Circuit Breaker Lightning Arresters | Fuses Reclosers Sectionalizers | Reclosers | Circuit-breaker at feeder head Fuse on MV/LV transformer | Circuit Breakers Fuses Lightning Arresters | Fuses Recloses | Fuses Lightning Arresters | Circuit Breakers Fuses Lightning Arresters Reclosers Sectionalizers | Circuit Breakers Reclosers | Circuit breakers Lightning Arresters | Reclosers | Fuses Reclosers (few but more being deployed) | Circuit Breakers Reclosers | Circuit Breakers | Fuses Reclosers | Fuses Reclosers | Circuit Breakers Fuses Reclosers Lightning Arresters | Circuit Breaker Lightning Arresters
21 |  | Transformer Connections |  |  | Delta-Delta Delta-Wye Wye-Delta Wye-Wye | Delta-Delta Delta-Wye Wye-Delta Wye-Wye | Wye-Wye | Delta-Delta Delta-Wye Wye-Delta Wye-Wye | Wye-Wye | Delta-Wye | Delta-Wye | Wyw-Wye (Grounded) | Delta-Wye | Delta-Wye (Grounded) | Data was not readily found. | Delta-Wye | Delta-Delta Wye-Delta | Delta-Wye (grounded) | Delta-Wye | Wye-Delta | Delta-Wye (grounded) | Delta-Delta Delta-Wye Wye-Delta Wye-Wye V-V Open Delta | Delta-Wye | Delta-Wye (Grounded) Wye-Wye (Grounded) | Delta-Delta Delta-Wye (Grounded) Wye-Delta Wye-Wye V-V Open Delta (Legacy) | Delta-Wye | Delta-Delta Wye-Delta | Delta-Wye | Wye Wye (Grounded) | Wye-Wye | Delta-Wye | Detla-Wye (Grounded) Wye-Wye (Grounded) | Wye-Delta | 33/11 kV: Delta-Wye 66/11 kV: Delta-Wye | Detla-Wye (Grounded) Wye-Wye (Grounded)
22 |  | DERs MV Level | Type |  | Batteries EV PV | Batteries EV PV | Batteries Combined Heat and Power (CHP) EV PV | Batteries EV PV | PV | PV | PV | Batteries PV Small Hydro Wind | Batterieis EV PV | Batteries PV | PV Small Hydro Wind | Batteries Combined Heat Power (CHP) EV PV | PV Small Hydro Batteries (since 2024) | Batteries PV Solar | EV | PV EV Wind | Batterieis PV Wind | Batteries PV Wind | Diesel Generators | PV Small Hydropower in rural areas | Batteries EV PV Small Hydropower in rural areas Wind | Batteries EV PV | Batteries PV Small Hydropower Wind | Combined Heat Power (CHP) PV Small Hydropower Wind | Batteries PV Over 1GW installed as 2025, representing 1/3 of the peak island load. | PV (limited) | Batteries PV | Batteries PV | Batteries EV PV | PV (Off Grid) | Biomass PV Wind
|  |  | Utility/Non-utility owned |  | Utility and non-utility owned | Utility and non-utility owned | Non-utility owned | Utility and non-utility owned | Utility and non-utility owned | Utility and non-utility owned | Utility and non-utility owned | Utility and non-utility owned | Utility and non-utility owned | Non-utility owned | Utility owned | Utility and non-utility owned | Non-utility owned | Utility and non-utility owned | Utility and non-utility owned | Non-utility owned | Non-utility owned | Utility and non-utility owned | Utility owned (except EDZ) | Utility and non-utility owned | Utility and non-utility owned | Utility and non-utility owned | Utility and non-utility owned | Non-utility owned | Non-utility owned | Non-utility owned | Non-utility owned | Non-utility owned | Utility and non-utility owned | Non-utility owned | Non-utility owned
|  |  | Visibility/Metering scheme |  | Smart Meters | Mostly Revenue Meters, Smart Meters at a few locations | SCADA | Mostly Revenue Meters, Smart Meters at a few locations | SCADA | Data was not readily found. | Data was not readily found. | SCADA Smart meters | Smart Meters | AMI/AMR to DMS SCADA | Data was not readily found. | Advanced metering/smart meters | SCADA | Smart Meters | Data was not readily found. | SCADA to DER > 500 kW | Smart meters | Smart Meters | Revenue Meters | Smart Meters | Residential: Revenue Meters, transitioning to Smaart Meters. >50% as of 20275 Commercial: Visibility at certain kW and MW scales (varies by utility) | SCADA Smart Meters | Revenue Meters SCADA | < 1MW: Revenue Meter > 1 MW: SCADA | SCADA at >38 kV | Smart Meters | None | SCADA | SCADA Smart Meters | Smart Meters for Bulk Customers | Smart Meters
|  |  | Grid services provided |  | Active Power | Active Power | Active Power Power Quality | Active Power | Active Power | Active Power | Data was not readily found. | Active Power | Active Power | No services | Data was not readily found. | Active Power Reactive Power (pilots) | Active Power Power Quality | - | - | Some services to TSO. | In accordance with CEI 0-16 grid interface requirements | Active Power | Active Power | Active Power | Active Power | Active power Frequency regulation | Active Power Reactive Power | Active Power Reactive Power | None. Recent adoption of 1547. One VPP that works as DR. | Active Power | None | Active Power Power Quality | Active power Frequency regulation | Active Power | Active Power
23 |  | Line Sensing/Monitoring/SCADA/ Control | Media |  | Cellular (3G and 4G) Fiber Optic Cable UHF Digital Radio Network | Copper Cable Cellular (3G and 4G) Fiber Optic Cable | Fiber Optic Cable Coaxial Cellular (4G) | Cellular (3G and 4G) Copper Cable Fiber Optic Cable | Cellualr (3G) Radio (General Packet Radio Service) | Cellular (4G and 5G) Fiber Optic Cable | Cellular (3G and 4G) Fiber Optic Cable | Fiber Optic Cable Radio UHF Wireless | Cellular (3G and 4G) Fiber Optic Cable | None | Data was not readily found. | Cellular (3G and 4G) Fiber Optic Cable Microwave Power Line Carrier (PLC) | Copper Cable Fiber Optic Cable Power Lne Carrier (PLC) | Cellular (4G and 5G) Copper Cable Fiber Optic Cables | Cellular (4G) Fiber Optic Cable | Cellular (3G and 4G) Fiber Optic Cable Sattelite | Fiber Optic Cable Wireless (GSM) | Cellular (3G and 4G) Copper Cable Fiber Optic Cable Power Line Carrier (PLC) | Cellular (4G and 5G) Fiber Optic Cable | Nothing | Cellular (4G and 5G) Copper Cable Fiber Optic Cable Microwave Power Lne Carrier (PLC) Satellite Radio Telephone (POTS) WiMax | Fiber Optic Cable | Cellular (3G and 4G) Fiber Optic Cable Power Line Carrier (PLC) Telephone (POTS) | Cellular (4G and 5G) | Fiber Optic Cable | Copper Cable Fiber Optic Cable | Copper Cable | Fiber Optic Cable Cellular (3G) | Cellular (4G and 5G) Copper Cable Fiber Optic Cable Power Lne Carrier (PLC) | Fiber Optic Cable | Copper Cable Fiber Optic Cable Microwave Power Line Carrier (PLC)
|  |  | Measured Information and Cycle |  | Active Power Alerts and Alarms Current Reactive Power Status (Breakers, reclosers, regulators, etc.) Voltage Cycle: seconds | Active Power Alerts and Alarms Current Reactive Power Status (Breakers, reclosers, regulators, etc.) Voltage Cycle: seconds | Active Power Current Reactive Power Voltage Cycle: not avaiable | Active Power Alerts and Alarms Current Reactive Power Status (Breakers, reclosers, regulators, etc.) Voltage Cycle: seconds | Active Power Alerts and Alarms Current Reactive Power Status (Breakers, reclosers, regulators, etc.) Voltage Cycle: 5 seconds | Active Power Alerts and Alarms Current Reactive Power Status (Breakers, reclosers, regulators, etc.) Voltage Cycle: 5 seconds | Active Power Current Reactive Power Voltage Cycle: not avaiable | Active Power Current Reactive Power Status (breaker, recloser, switch, etc.) Voltage Cycle: 30 seconds | Active Power Alerts and Alarms Current Reactive Power Status (Breakers, reclosers, regulators, etc.) Voltage Cycle: 2-300 seconds (Standard) | No | Data was not readily found. | Current Voltage Cycle: not avaiable | Active Power Current Reactive Power Voltage Cycle: not avaiable | Active Power Alerts and Alarms Current Frequency Reactive Power THD Voltage Cycle: One second | Active Power Alerts and Alarms Current Frequency Power Factor Reactive Power Status (Breakers, reclosers, regulators, etc.) Voltage Cycle: not avaiable | Current Voltage Cycle: not avaiable | At the head of the feeder: Voltage, Active Power, Reactive Power, Current, Alerts and Alarms, Frequency, Status (Breakers, regulators, etc.) Cycle up to 1 second | Current Harmonics Voltage Cycle: Every minute to 1 hour (In case of low speed communication such as copper cable or PLC). Every 1 second to 30 seconds (In case of high speed communication network such as Fiber Optic) | Current Status (breaker, recloser, switch, etc.) Voltage Cycle: Every few seconds | Nothing | Minmal Outside of substation. Within subsetation: Active Power Alerts and Alarms Current Reactive Power Status (Breakers, reclosers, regulators, etc.) Voltage Cycle: by exception, typically 2-300 seconds PMU: 30–60 samples/sec | Data was not readily found. | Active Power Alerts and Alarms Current Reactive Power Status (Breakers, reclosers, regulators, etc.) Voltage Cycle: seconds | Data was not readily found. | Breaker status Current Voltage Cycle: not avaiable | Active Power Reactive Power Cycle: 30 minute peak | NA | Active Power Current Reactive Power Voltage Cycle: On change of value | Voltage Cycle: 30 seconds | Data was not readily found. | Active power Current Reactive power Voltage Cycle time: SCADA: 2–10 seconds PMU: 30–60 samples/sec
|  |  | Available Control type |  | Open/close breaker, switch, and/or recloser | Open/close breaker, switch, and/or recloser | Open/close on switchgear | Open/close breaker, switch, and/or recloser | Open/close breaker, switch, and/or recloser | Open/close breaker, switch, and/or recloser | Open/close breaker, switch, and/or recloser | Open/close breaker, switch, and/or recloser Protection on/off | Open/close breaker, switch, and/or recloser Raise/lower regulator | No | Data was not readily found. | Open/close breaker, switch, and/or recloser | Open/close breaker, switch, and/or recloser Raise/Lower to Voltage Regulator | Open/close breaker, switch, and/or recloser | Open/close breaker, switch, and/or recloser | Open/close breaker, switch, and/or recloser Protection on/off | Open/close breaker, switch, and/or recloser | Open/Close to sectionalizer, Raise/lower regulator | Open/close breaker, switch, and/or recloser Open/close capacitor | Nothing | Open/close breaker, switch, and/or recloser Open/close capacitor Raise/Lower to Voltage Regulator | Open/close breaker, switch, and/or recloser Raise/Lower to Voltage Regulator | Open/close breaker, switch, and/or recloser | Open/close breaker, switch, and/or recloser | Open/close breaker, switch, and/or recloser Raise/lower regulator or OLTC | Open/close breaker, switch, and/or recloser Raise/Lower to Voltage Regulator | Open/close breaker, switch, and/or recloser Raise/Lower to Voltage Regulator | Open/close breaker, switch, and/or recloser | Open/close breaker, switch, and/or recloser Raise/Lower to Voltage Regulator | Open/close breaker Raise/Lower to Voltage Regulator | Open/close breaker, switch, and/or recloser Raise/Lower to Voltage Regulator
|  |  | Communication Protocols |  | DNP 3.0 IEC 61850 | DNP 3.0 IEC 61850 | IEC104 MODBUS | DNP 3.0 IEC 61850 | DNP 3.0 IEC 61850 | DNP 3.0 IEC 61850 | DNP 3.0 IEC 61850 Modbus | DNP 3 Modbus | IEC 60870-5-104 IEC 61850 IEC 60870-5-101 DNP 3 Modbus | No | Data was not readily found. | DNP 3 IEC 61850 | DNP3.0 IEC61850 | IEC60870-104 (most common) ModBus RS-485 TCP/ IP | DNP 3.0 IEC 61850 IEC 60870-5-101 IEC 60870-5-104 | IEC 60870-5-101 | IEC 60870-5-104 IEC 61850 Modbus RS485 TCP/IP | Custom/Proprietary (X.25/CDT/HDLC) IEC61850 | DNP3 IEC 60870-5-104 IEC 61850 | Nothing | Custom/Proprietary DNP GOOSE IEC 61850 IEC 60870, and other IEC standards IEEE 802.3/802.2 Modbus TCP/IP | DNP IEC 61850 | IEC 60870-5-101, IEC 60870-5-104, DNP3, Modbus, IEC 61850 | IEC 104 Legacy protocols (phasing out) | DNP Modbus | IEC 61850 | IEC 101 for SCADA | DNP3 ICCP IEC104 Modbus | DNP IEC61850 | IEC 60870-5-101 IEC 60870-5-104 Modbus | DNP3 IEC 61850 IEC 60870-5-104 Modbus OPC UA
| System Section | Characteristic | Sub-category (if applicable) |  | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values | Typical Values
24 | Secondary | Voltages (line-to-ground) | Residential |  | 230 V | 127, 220, 380 V (phase to phase) | 230/400V | 127, 220, 380 V (phase to phase) | 220 V (phase to neutral) | 220 V | 120 V Single Phase 150 V Single Phase 120/240 V Splt Phase 120/208 V 2 Phase 120/208 V 3 Phase 150/260 V 3 Phase | 120/240 V | 220/380 V | 230 V | 400 V | 230 V | 120/240 V Split Phase | 230/415 V | 230 V | 230/400 V | 230 V | 100/200 V | 230 V (line-to-neutral) | 230 V single phase 400 V three phase | 120/240 V Split Phase | 230 , 415V | 230, 400 V | 230 V | 120/240 V Split Phase | Old system: 127/220V. New system: 230/400V or 220/380V. | 230, 400V | 230 V | 110, 220, 380V | 230/433 V | 230 V
|  |  | Commercial |  | 230 V | 127, 220, 380 V (phase to phase) | 230/400V | 127, 220, 380 V (phase to phase) | 220 V (phase to neutral) | 220 V | 120/240 V Split Phase 120/240 V Three Phase 120/208 V Three Phase 220/380 V Three Phase 254/440 V Three Phase 270/480 V Three Phase | 120/240 V 277 V | 220/380V | 230 V | 400 V | 230 V | 120/240 V Split Phase 240/480 V Split Phase 120/208 V 3 Phase 277/480 V 3 Phase | 230/415 V | 230 V | 230/400 V | 230 V | 100/200 V | 230/400 V (standard supply) | 230 V single phase 400 V three phase | 120/240 V Split Phase 240/470 V Split Phase 120/208 V 3 Phase 277/450 V 3 Phase | 415V | 230, 400 V | 230 V | 120/240 V Split Phase 240/470 V Split Phase 120/208 V 3 Phase 277/450 V 3 Phase | Old system: 127/220V. New system: 230/400V or 220/380V. | 415 V, 6.6, 22 kV | 230 V | 110, 220, 380V | 230/433 V | 230/400 V
|  |  | Industrial |  | 230 V | 127, 220, 380 V (phase to phase) | 230/400V | 127, 220, 380 V (phase to phase) | 380 V (phase to phase) | 220 V | 120/240 V Split Phase 120/208 V 3 Phase 220/280 V 3 Phase 254/440 V 3 Phase 270/480 V 3 Phase | 120/240 V 277 V | 220/380V | Data was not readily found. | 400 V | 230 V | 120/240 V Split Phase 240/480 V Split Phase 120/208 V 3 Phase 277/480 V 3 Phase | 230/415 V | 230 V | 230/400 V | 230 V | 240/415 V | 400 V; large industrial fed from MV | 400 V three phase 11 kV, 33 kV, 66 kV 1 consumer in 132 kV | 120/240 V Split Phase 120/208 V 3 Phase 277/450 V 3 Phase 347/600 V 3 Phase | 415V , 22kV. | 230 V, 400 V, 11 kV | 230 V | 120/240 V Split Phase 120/208 V 3 Phase 277/450 V 3 Phase 347/600 V 3 Phase | Data was not readily found. | 415 V, 6.6, 22 kV | 600 V | 110, 220, 380V | 230/433 V | 400 V
25 |  | Typical Secondary Length |  |  | <500 m | <750 m | 400-600 m | < 750 m | .25-1.5 km | 250-500 m | Data was not readily found. | 240 m | 1.0 km | Data was not readily found. | 20-500 m | Rural: <10 km Urban: .5-5 km | 200 m | Rural: <5 km Urban: <1 km | Data was not readily found. | Data was not readily found. | 100-800 m | < 50 m | Rural: < 1,000 m Urban: 200-500 m; | Rural < 5 km Urban < 1 km | 10-150 ft. | 250 meters | 0-1500 m | 100 m | 10-150 ft. | Data was not readily found. | NA | 200 m | 100-1000 m | Data was not readily found. | 0.1–1 km
26 |  | Typical types of Conductors |  |  | Overhead: bare wire and insulated AAC: 19/3.25, copper in older areas. XLPE: insulation over each of four aluminium cores. Typical conductor sizes are 95 mm2 and 150 mm2 Underground: XLPE Al: 185 mm2 and 240 mm2 | Overhead: bare zinc plated steel conductor | Data was not readily found. | Aluminium; 1/0 AWG; 2/0 AWG; 4/0 AWG; 336,4 MCM; or Multiplex 35 mm2; 50 mm2; 70 mm2; 120 mm2 | Most common: Al: 50 mm2 Cu: 17 mm2 | Overhead: bare wire and insulated Overhead: LGJ-35 JKLGYJ-10-240/30 Underground: YJV、YJV22、YJV32、YJV42 | Data was not readily found. | Overhead: AAAC 123.3 kcmil and 155.4 AAAC AAC 3/0 AWG Underground: PVC 2 AWG ~ 1000 kcmil | Data was not readily found. | Data was not readily found. | Data was not readily found. | 0.1 to 2 ohms/km | Overhead: AAC 6 AWG ~ 4/0 AWG Underground: XLPE 2 AWG ~ 1000 kcmil | Overhead: ACSR: Racoon, Dog, Rabbit common Underground: XLPE Al: 10 - 300 mm2 | Overhead: NFAAX-T 35, 50, 70 mm2 AAC, AAAC, BCC 25, 35, 50 mm2 Underground: NYFGbY, NYAFGbY 25, 35, 50, 70, 95 mm2 | Overhead: AAC 25-120 kcmil | Overhead: Al - XLPE 35, 70 mmq Underground: Al - XLPE 50, 95, 150, 240 mmq | Vinyl wire (DV): 14 or 22 or 38 mm2 | Overhead: AAC: 122-475 kcmil ACSR: 122-475 kcmil Underground XLPE, ABC at LV: 122-475 kcmil | Overhead: ACSR ABC conductor DOG/RABBIT/WEASEL Underground: XLPE | Duplex, triplex, and quadaplex 6 AWG to 336, insulated | AAAC (no size details). | Overhead: ACSR: Racoon, Dog, Rabbit common Underground: XLPE Cu: 300 | Data was not readily found. | Duplex, triplex, and quadaplex 6 AWG to 336, insulated | Data was not readily found. | Overhead: 4*300 mm2 Cu Underground: XLPE/DSTA/PVC | Data was not readily found. | Overhead: ACSR 6 AWG ~ 336 kcmil AAC 6 AWG ~ 1/0 AWG Underground: XLPE 2 AWG ~ 1000 kcmil PVC 2 AWG ~ 500 kcmil USE 2 AWG ~ 250 kcmil | Data was not readily found. | Data was not readily found.
27 |  | Voltage Regulation Devices |  |  | Manual tap adjustment of transformer Shunt Capacitors Voltage Regulators | Manual tap adjustment of transformer | Underload tap changers (ULTC) Volage Regulators (limited) | Manual tap adjustment of transformer | Manual tap adjustment of transformer | Underload tap changers (ULTC) Volage Regulators | Data was not readily found. | Manual tap adjustment of transformer | None | Off-load tap changers | Capacitor banks Manual tap adjustment of transformer | Capacitor banks Voltage Regulators | Capacitor banks | None | Manual tap adjustment of transformer | None | Off-load Tap Changer (MV side) | Manual tap adjustment of transformer | None | Manual tap adjustment of transformers | Manual tap adjustment of transformer Shunt capacitors | Manual tap adjustment of transformer (Some commerical units) | On-load Tap Changers (OLTC) Shunt Capacitors | Some Off-load tap changers | Manual tap adjustment of transformer Shunt capacitors | None | Off-load tap changer at LV side of 22/LV or 6.6/LV transformers | Off-load tap changers | Manual tap adjustment of transformer (Some commerical units) | None | Capacitor banks Voltage Regulators
28 |  | Protection Devices |  |  | Fuses | Fuses | Fuses | Fuses | Fuses | Fuses | Fuses | Fuses | Circuit Breaker Fuses | Fuse towards distribution transformer | Circuit Breaker Fuses lightning arrester | Fuses Switches | Fuses | Circuit Breaker Fuses | Fuses | Fuses | Circuit Breakers | Fuses | Fuses | Circuit Breakers | Fuses | Circuit Breakers | Circuit Breakers Fuses | Fuses | Fuses | Fuses | Fuses | Fuses | Fuses | Circuit Breakers Fuses | Circuit Breakers Fuses
29 |  | Transformer Connections |  |  | For three-phase: Delta-Wye and Wye-Wye For SWER: Split-Phase | Delta-Wye | Delta-Wye | Delta-Wye | Wye-Wye (grounded) | Delta-Wye | Delta-Wye Wye-Wye | Wye-Wye | Delta-Wye | Delta-Wye (Grounded) | Delta-Wye | Wye-Wye | Center-tap Delta-Wye Wye-Delta | Delta-Wye Wye-Wye | Delta-Wye | Delta-Wye (3 phase) Wye-Wye (Single phase) | Delta-Wye (grounded) | Delta-Delta Delta-Wye Wye-Delta Wye-Wye V-V Open Delta | Delta-Wye | Delta-Wye | Center-tap Delta-Delta Delta-Wye Wye-Delta Wye-Wye V-V Open Delta (Legacy) | Delta-Wye | Delta-Wye | Delta-Wye | Center-tap Delta-Delta Delta-Wye Wye-Delta Wye-Wye | Wye-Wye | Delta-Wye | Delta-Wye Wye-Wye | Wye-Delta | Delta-Wye | Delta-Wye
30 |  | Transformer kVA rating |  |  | 5-2000 kVA | Up to 300 kVA (45 kVA, 75 kVA, and 112.5 kVA are common) | 160 - 630 kVA (mainstream now is 400/630) | Up to 300 kVA (45 kVA, 75 kVA, and 112.5 kVA are common) | 75- 1000 kVA. Average value: 500 kVA, Median value: 300 kVA (values for the capital, Santiago) | 5-250 kVA | Single Phase: 3, 5, 10, 15, 25, 37,5, 50, 75 kVA. Three Phase: 15, 30, 45, 75, 112,5 kVA | 10-1000 kVA | 25-2500 kVA | 630, 800, 1000 kVA | Data was not readily found. | 500-800 kVA | 15-1000 kVA | Three phase: 25,100,400,630,990,1600, 2000 kVA | 5-2000 kVA | Two Phase: 5,15,33 KVA Three Phase: 50, 100, 200 ,400, 630 and 1000 KVA | 50, 100, 150, 250, 400, 630 kVA (others 160, 200, 315 kVA) | 5-100 kVA | 100, 160, 250, 400, 630 kVA | 25 kVA- 1000 kVA | 5-2500 kVA | 1000~4000 kVA. Below 500kVA - mainly residential and commercial | 10-600 kVA | 50-1000 kVA | 5-1000 kVA | 300, 500, 1000, 1500 KVA | 1000, 1500 kVA | Data was not readily found. | 5~4000 kVA | 100-1000 kVA | 25–630 kVA
31 |  | Average Number of Customers Served per Service Transformer | Residential |  | 1-230 | 16 | average 55 combined | 16 | 70-150 | 1-150 | 20-100 | 30 | 10-100+ | 200 | No information due to confidentiality | 10-200 | 1-25+ | 20-500 Delhi average (~250) | Data was not readily found. | Two Phase: 3 Three Phase (upto 400 kVA): 27 Three Phase (400-1000 kVA): 50 | Very variable: Domestic users up to 600 Other uses (eg public lighting, ev chargers, etc) up to 200 | 20-100 | 30-100 | 100-500 | 1-25+ | 50-100 | Urban Area (50–200 kVA): ~20-100 Household Rural Areas (50–200 kVA): ~10–40 Household | 100 | 1-25+ | about 10 | Data was not readily found. | 60 | 100-200 | 10-100+ | 20–100+
|  |  | Commercial |  | 1-100 | 1 | see above | 1 | 1-10 | 1-30 | 1-30 | 10 | 1 | 1-20 |  | 5 to 20 | 1-5 | 1~30 | Data was not readily found. | Two Phase: 0 Three Phase (upto 400 kVA): 2 Three Phase (400-1000 kVA): 11 | Data was not readily found. | 1 | 5-30 | 10-20 consumers with more than 40 kVA load generally have own transformer | 1-10 | 1 (depending on type of projects) | Urban Areas (100–500 kVA) : 15-100 shops/offices Rural Areas (100–500 kVA): 5-40 shops/offices | 3 | 1-10 | 1 | Data was not readily found. | 1-5 | 20-50 | 1 | 10–50
|  |  | Industrial |  | 1-50 | 1 | see above | 1 | 1 (typically each industrial customer has its own MV/LV transformer) | 1-15 | 1-5 | 1 | 1 | 1 |  | 1 to 10 | 1 | 1~10 | 1 | Two Phase: 0 Three Phase (upto 400 kVA): 0 Three Phase (400-1000 kVA): 1 | Data was not readily found. | 1 | 1-5 | 1 to 10 | 1-5 | 1 (depemnding on type of projects) | 1-2 | Data was not readily found. | 1-5 | 1 | 1 (At least 2 transformers in parallel) | 1 | 5-10 | 1 | 1–5
32 |  | Typical Load Size | Residential |  | 3.5-6.5 kVA | 5 kVA | Most common: 9.2 kVA / 17.3 kVA | 5 kVA | 6 kVA-10 kVA | 1.5-3 kVA | 3-20 kVA | 2 kVA | 2-8 kVA+ per 100 m2 (or 1-500 kVA) | 4-140 kVA | No information due to confidentiality | 1-2 kVA | 1-5 kVA | National average: 1.24 kW | 900 VA - 6.6 kVA | Old: 0-29 kVA New: 12-29 kVA | 1-25 kVA (single phase up to 9.9 kVA) | ＜50kVA (Typical 3kVA～10kVA) | 0.5-2 kW per household | 1-10 kVA | 1-25 kVA | <150kVA Residential complex and small commerical complex | 25, 50, 100, 200 kVA | 3.45-6.9 kVA | 1-25 kVA | 1-25 kVA | NA | 4-20 kVA | Data was not readily found. | Data was not readily found. | 3–10 kW
|  |  | Commercial |  | 15 kVA | 8 kVA | 25-56 kVA | 8 kVA | 10-100 kVA (47 Average) | 3-10 kVA | 3-75 kVA | 10 kVA | 5-10 kVA+ per 100 m2 | 35 kVA-10 MVA |  | few kilowatts (e.g., small shops or offices) to several hundred kilowatts (larger businesses) | 37-225 kVA | National average: 3.34 kW | Category 1: 6.6-200 kVA Category 2: >200 kVA | 3-49 kVA, 20 kVA (avg) | 200 kVA max LV 9.99 MVA max MV | 50kVA-2MVA | 10-100 kW depending on business | 10-40 kVA | 10-250 kVA | 150, 250, 500 kVA | 10, 15, 25, 50, 100 kVA | 40 kVA | 10-250 kVA | 10 kVA-2 MVA | NA | >43 kVA | Data was not readily found. | Data was not readily found. | 10–100 kW
|  |  | Industrial |  | 45 kVA for light industrial in LV network | 13 kVA | not on LV grid (see primary), we serve customers up to 25 MW | 13 kVA | 100-500 kVA (207 Average) | >100 kVA | 0.1-5 MVA | 200 kVA | ＞ 2 MVA | 0.5-10 MVA |  | 0.5MVA to 5 MVA (medium industries), and 5 MVA to 50 MVA large industries | >225 kVA | National average: 15.67 kW | >200 kVA | >=50 kVA, 126 kVA (avg) | 200 kVA max LV 9.99 MVA max MV | ＞2MVA | 20-200 kW (for LV-fed industries) | 10-50 MVA | 100 kVA+ | >500kVA, supply on 22kVA through switchgear panel | 200, 400, 600 kVA | NA | 100 kVA+ | 1-100 MVA | NA | 1-10 MVA | Data was not readily found. | ＞1 MVA | >100 kW
|  |  | Smart meters | Percentage penetration | Per state and territory (2025): Victoria: ~100% New South Wales: ~39% South Australia: ~46% Queensland: ~43% Northern Territory: ~27% Western Australia: ~42% Tasmania: ~78% Australian Capital Territory: ~40% | neglectable, some utilities have smart meters at every MV customer | 60%+ roll-out. Finished by 2028 | neglectable, some utilities have smart meters at every MV customer | <10%. Loads connected to distribution networks can decide to have an smart meter (it is not compulsory). Thus, most of residential customers do not have an smart meter. On the contrary, most of the commercial and industrial customers have one (mainly to get a better control of their consumption and the corresponding bill) | By December 2022, the number of smart meters in China has exceeded 650 million, nearly 100% | <1% Primarily conventional metering. Some utilities are currently deploying smart meters. | 49% - 2023 | About 213000 smart meters were installed and operated, and the system bills were issued for about 189000 meters. On July 2021, a tender was issued to install about 530000 smart meters at level of distribution network. The technical and financial bids have been completed. A nother contract for installing 1.6 million smart meteres is under review. | 100 % smart meters P2P, Mesh with 4G connection |  | around 62% | Data was not readily found. | As of December 2025, ~15% penetration is achieved but the speed is very fast. Govt target is to achieve 95% penetration by 2026 | Only around 500,000 customers in Bali. | Data was not readily found. | over 95 % | At the end of March 2021, the installation rate exceed 85% nationwide, and is scheduled to reach 100% within fiscal year 2024 | Around 1.1 million installed post-2012; Power Line Carrier | Around 4%. Smart meters being rolled out | R: billing or none C: smart meter, billing, or none I: power quality, smart meter, billing, or none | As at 2023, 17% of renewable energy has been completed and commissioned. New project in the pipeline. Target renewable energy is to occupy 60% of the grid. | As of 2023 5%–7% of the total electricity meters. | 100% coverage at the end of 2024 | Smart meters most of which connected through AMR (power line carrier) | 100% Complete Smart Meters Communication Through 4G Network SMOC: Smart Meter Operating Center is monitoring all the smart meters. | Data was not readily found. | P2P meters and AMI | As of May 2020, 43 percent of the target has been reached. Latest data is not available. | All customers are connected through PLC meters. Bulk customers are connected through smart meters | As of 2016, Turkey installed approximately 4.6–4.7 million smart meters per year
|  |  |  | Sampling frequency | 5 minutes or 30 minutes, depending on distribution company | 15 min |  | 15 min | 15 minutes | 5 minutes or 15 minutes,it depends on the application scenario and system design requirements. | Data was not readily found. | 15 minutes |  |  |  | 30 mins (smart meters) | Data was not readily found. | 15 minutes | Data was not readily found. | 30 minutes | 15 minutes | The cycle is 30 minutes now. Next-generation smart meters that will be applied from year 2025 will newly support 5-minute and 1-minute cycles. | Data was not readily found. | Data was not readily found. | 5 or 15 minutes is the most common. With some newer models supporting 1 minute, and higher rate power quality fucntions. | Each 10 minutes | Every 15 minutes | Data was not readily found. | Data was not readily found. |  | Data was not readily found. |  | 15 min. or 30 min. |  | Data was not readily found.
|  |  |  | Data transmission frequency | Once a day, or every 6 hours, or every 15 minutes, depending on the distribution company | N/A |  | N/A | As 2025, there isn´t a compulsory standard. Since there are few smart meters deployed, the data is usually retrived once a day | 5 minutes or 15 minutes,it depends on the application scenario and system design requirements. | Data was not readily found. | Daily |  |  |  | Daily (default), half-hour (opt-in) | Data was not readily found. | Data was not readily found. | Data was not readily found. | 30 minutes | Daily | ・For 30 minute values, transmit within 60 minutes ・For 5-minute values, transmit more than 3% of customers within 10 minutes | Data was not readily found. | Data was not readily found. | Once or more daily | Not available | Once per hour (or every 15 minutes for priority customers) | Data was not readily found. | Data was not readily found. |  | Data was not readily found. |  | 15 min. or 30 min. |  | Data was not readily found.
|  |  | Demand response | Percentage participation | Not typical (there are some VPPs that are recruiting LV-connected demand response though) | none | Market flexibility under investigation/testing. Customers do have capacity tariff. | none | none | limited, no value available | Data was not readily found. | Unknown | None | None |  | Exact percentage unknown-challenges persist with DR adoption, however some old adopters of smart meters with technologies like EVs opt for DR | Data was not readily found. | Nascent stage. Only few utiliites are running DR programs with little participation | None | Trialling SMS opt in programme for customers to "turn up of turn down" | Research projects | Data was not readily found. | None | Estimated 2-3 % | Implmented at some utilities, as stand-alone programs or part of virtial power plants (VPP) | Data was not readily found. | <1 percent | Pilot project | One VPP in the island with aggregated DER of 17MW. Works as DR. | Almost none. Very few special customers are on automatic under-frequency load shedding | Data was not readily found. | Some large customers. | 4.4GW as of 2022. Estimated at 5%~10%. Accurate latest data is not available. | None | Limited
|  |  |  | Types of demand response programs | Not typical (there are some VPPs that are recruiting LV-connected demand response though) | none |  | none | none | Mostly used for Peak shaving and maintaining grid Balancing. Typically, direct contract is signed between utility and consumer, but in recent years, demand response through "aggregator" has become more common. | Differential tarifs in commercial areas | Time of Use (ToU) Tarrif |  |  |  | Time of Use (ToU) Tarrif, Capacity market (CM) DR for large industries, Some smaller programmes by few DNOs also include DSR, V2G, and Peak Shaving Programmes | Data was not readily found. | Mainly peak load shaving and load shifting as of now | None | Peak Shaving between 5pm and 7pm. Peak shifting sought | Research projects | Mostly used for Peak shaving and maintaining grid Balancing. ( Typically, direct contract is signed between utility and consumer, but in recent years, demand response through "aggregator" has become more common. ") | None | Time of Use (TOU) Tarriff Seasonal Tarriff | Critial Peak Pricing (CPP) Direct Load Control (DLC) Real Time Price (RTP) Time of Use (TOU) Virtual Power Plant (VPP) | Data was not readily found. | Time-of-Use (TOU) Tariffs, Pilot Projects for Advanced Demand Response | Data was not readily found. | Direct Load Control (DLC) Virtual Power Plant (VPP) |  | Data was not readily found. |  | Voluntary Demand Response, Reliability Demand Response, Plus Demand Response, National Demand Response, Frequency Demand Response |  | Time of Use (TOU)
33 |  | DERs LV Level | Type |  | Batteries EV PV | PV | Batteries EV PV | PV | PV | Batteries EV PV | PV | Batteries EV PV | Batteries PV EV | EV PV | PV | Batteries EV PV | Batteries PV | Batteries EV PV | EV PV | PV EV Wind | Batteries EV PV Wind | Batteries EV PV | Batteries Diesel generators PV | No DER at 400 V level | Batteries EV (limited) PV | Batteries EV PV | Batteries PV | PV | Batteries PV Over 1GW installed as 2025, representing 1/3 of the peak island load. | PV (limited) | PV | EV PV | Batteries EV PV | PV (off grid) | Batteries PV
|  |  | Utility/Non-utility owned |  | Utility and non-utility owned | Non-utility owned | Non-utility owned | Non-utility owned | Non-utility owned | Non-utility owned | Non-utility owned | Non-utility owned | Utility and non-utility owned | Non-Utility Owned | Utility and non-utility owned | Utility and non-utility owned | Non-utility owned | Non-utility owned | Non-utility owned | Non-utility owned | Non-utility owned | Non-utility owned | Non-utility owned | Data was not readily found. | Utility and non-utility owned | Utility and non-utility owned | Non-utility owned | Non-utility owned | Non-utility owned | Non-utility owned | Non-utility owned | Non-utility owned | Utility and non-utility owned | Non-utility owned | Utility and non-utility owned
|  |  | Visibility/Metering scheme |  | Smart Meters | Meter | Meter | Meter | PV and EV charging infrastructure connected to distribution networks must have advance metering infrastructure (AMI) | Sensor types to be determined | Data was not readily found. | SCADA Smart meters | Smart Meters for PV (Net energy meter, solar meter) | AMR/AMI cnection to DMS | Smart MeterS | Smart Meters | Smart Meter | Smart Meters | Export Import Meter | Smart Meters being rolled out. Data currently not available from same | Smart Meters | Smart Meters | Net-metered PV has visibility; generators do not. | Data was not readily found. | SCADA Smart meters | SCADA Smart Meters | Net metering | None-at the present time | all DER > 1MW | Smart Meters | None | Smart Meters | SCADA Smart meters | None | SCADA Smart meters
|  |  | Grid services provided |  | Active power | Active power | Active Power | Active power | Active power | Active power | Data was not readily found. | None | Active Power | No services | Active Power | Data was not readily found. | None-at the present time | Demand response | Active Power | Demand down being rolled out | In accordance with CEI 0-21 grid interface requirements | Active Power | Minimal; mainly backup and local supply | Data was not readily found. | Active Power | Active Power | Active Power Reactive Power | None-at the present time | Active Power | Active Power | None | Active power | Active power | Active Power | Active Power
34 |  | Line Sensing/Monitoring/SCADA/ Control | Media |  | Cellular (4G and 5G) Radio WiMAX | None | not available (apart from testcase) | None | None | Cellular (4G and 5G) Copper Cable | None | Interface with AMI | Cellular (3G and 4G) | Cellular | No information due to confidentiality | Fiber Optic Cable Microwave Power Line Carrier (PLC) | None | None | None | 2G via commercial provider | Cellular (4G and 5G) Copper Cable Power Lne Carrier (PLC) Radio | Connecting surrounding device using smart meter communication (Wire-less(920MHz/2.4GHz)) | Cellular (3G) for meters Power Line Carrier (PLC) for diesels | No sensing at 400 V level | Cellular (4G and 5G) Fiber Optic Cable Power Line Carrier (PLC) Radio | None | Cellular (4G and 5G) Telephone cables Fiber Optic Cable | Power Lne Carrier (PLC) | None | Coper Cable Fiber Optic Cable | None | Data was not readily found. | Cellular (4G and 5G) Copper cable Fiber Optic Cable Power Lne Carrier (PLC) | Cellular (4G) | Fiber Optic Cable Power Lne Carrier (PLC)
|  |  | Measured Information and Cycle |  | Active Power Current Reactive Power Voltage Cycle: 5 min. |  | not available (apart from testcase) |  |  | Active Power Current Reactive Power Voltage Cycle: 5 seconds |  |  | Active Power Current Reactive Power Voltage Cycle: Information not avaialble | Active Power Current Reactive Power Voltage Cycle: 15 minutes |  | Active Power Current Reactive Power Voltage Cycle: 5 to 30 minutes |  |  |  | Data was not readily found. | Smart Meter data Cycle: up to 15min | Connecting surrounding device using smart meter communication | Active Power Current Reactive Power Voltage Cycle: Daily | N/A | Limited due to short secondary systems. Residential:Smart Meter data reads and remote open/close. Industrial: SCADA connenction to larger DER or industrial. Cycle: 3-5 seconds |  | Active Power Current Reactive Power Voltage Cycle: 1min | 1x day |  | Active Power Cycle: 30 minutes |  | Voltage Cycle: 1 minutes | Voltage Cycle: 30 seconds | Bulk customer meter reads Cycle: Data was not readily found. | Current Energy Voltage Cycle;: 2–10 sec
|  |  | Available Control type |  | Open/close switch or recloser Raise/lower regulator |  | not available (apart from testcase) |  |  | Open/close switch or recloser |  |  | Open/close switch or recloser | Switch off/on |  | Open/close switch or recloser |  |  |  | Data was not readily found. | Open/close Smart Meter Reset status word Programming of the smart meter | Connecting surrounding device using smart meter communication (on/off) | Open/Close smart meter switch | N/A | Open/Close Smart Meter |  | Open/Close smart meter switch | Open/Close smart meter switch |  | Open/Close smart meter switch |  | Open/close recloser Raise/lower regulator | Open/Close to recloser Raise/Lower to Voltage Regulator | Data was not readily found. | Local, limited remote control
|  |  | Communication Protocols |  | DNP 3.0 IEEE 802.16 |  | not available (apart from testcase) |  |  | DNP 3.0 IEC61850 |  |  | IEC 60870-5-104 IEC 61850 IEC 60870-5-101 Modbus | Data was not readily found. |  | DNP 3 IEC 61850 |  |  |  | Data was not readily found. | Modbus RS485 TCP/IP | ISO/IEC14543-4-3 | DNP DLMS/COSEM, IEC 60870-5-104 Power Line Carrier (PLC) | N/A | IEC62056 TCP/IP |  | The LV networks are not monitored neither are controlled by the DNO | COSEM DLMS |  | IEC 104 IEC 101 MODBUS RTU |  | DNP3 ICCP IEC104 MODBUS. | DNP3.0 IEC61850 | Data was not readily found. | DLMS/COSEM IEC 62056 Modbus